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FAO: Liz Harrison  
Planning Department  Eastleigh Borough Council Eastleigh House  
Upper Market St  
SO50 9YN  

Sent Electronically only
Thurs 22nd June 2023


Discharge of condition 14 of full planning permission F/19/86233   
Land to the North and East of Boorley Green, Winchester Road, Botley, SO32 2UA 
We are submitting the revised documents in relation to condition 14 application ref: DC/23/94165.  

Condition 14 – Commercial to Residential Sound Insulation
Reports accompanying application: 
L1424.3 V4 - Commercial to Residential Sound Insulation
L1424.4 V1 - BREEAM HEA 05 shell – core assessment
EHO stated the following:
 Condition 14 requires a sound insulation performance between retail space and dwellings within the same building.
The required sound insulation is 60 dB DnTw.
However, we do not find information on this in the application documents. It appears the applicant has confused internal separation sound insulation between retail and dwellings with façade sound insulation, which is all together different to the require of Condition 14.
We suggest the applicant looks into this again and either provides calculated or measured performance between occupied spaces demonstrating the performance is 60 dB DnTw or better.
Our acoustic consultant has reviewed these comments and has responded to say that the HEA 05 report is based on the BREEAM requirements for internal noise in the retail spaces. Both reports submitted are titled accordingly.

A commercial to residential assessment has been provided and accompanies this letter, which includes the calculation method in the appendix of the report. This report states that the proposed design is expected to meet the design requirements.
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